## RH
OUR WATER MEETS THE REQUIREMENTS OF SANS 241-2:2015
Area Tested | Redelinghuys - Municipal office
Date
| Range | 2019-07-02 | 2019-07-16 | 2019-08-13 | 2019-08-27 | 2019-09-10 | 2019-09-25 | 2019-10-08 | 2019-10-23 | 2019-11-12 | 2019-11-26 | 2019-12-11 | 2019-12-23 | 2020-01-14 | 2020-01-28 | 2020-02-11 | 2020-02-25 | 2020-03-10 | 2020-03-24 | 2020-04-07 | 2020-04-21 | 2020-05-12 | 2020-05-26 | 2020-06-09 | 2020-06-23
pH | ≤5 - ≤9.7 | 6.84 | 6.9 | 6.84 | 7.01 | 6.7 | 6.79 | 6.71 | 6.81 | 6.67 | 6.81 | 6.87 | 6.77 | 6.71 | 6.68 | 6.86 | 6.88 | 6.66 | 6.77 | 6.81 | 6.69 | 6.3 | 6.69 | 6.66 | 6.69
Conductivity | ≤170 | 97.3 | 96.3 | 97.8 | 93.6 | 92.4 | 92.2 | 78.6 | 88.7 | 87.9 | 89.3 | 84.9 | 77.3 | 67.3 | 65.4 | 72.5 | 66.7 | 61.2 | 72.9 | 75 | 67.5 | 66.9 | 86.8 | 88.8 | 85.8
Turbidity | ≤5 | 0.35 | 0.59 | 0.36 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | 0.39 | 0.41 | 1.6 | 0.47 | 0.7 | 0.41 | 0.59 | <0.32 | 0.67 | 0.38 | 0.6 | <0.32 | <0.32 | <0.32 | <0.32
Colour | ≤15 | <10 | 11 | <10 | 15 | 11 | 15 | <10 | <10 | <10 | <10 | <10 | 13 | 12 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 16.5 | 17.1 | 17.6 | 17.5 | 15.2 | 15.7 | 15.2 | 18.1 | 16.1 | 14.5 | 16.3 | 14.6 | 11.6 | <0.50 | 16 | 27.1 | 11.6 | 13.5 | 11.3 | 10.8 | 12 | 16 | 16.3 | 16.1
Chloride | ≤300 | bar: 2019-07-02 to 2020-06-23
Flouride | ≤1.5 | bar: 2019-07-02 to 2020-06-23
Dissolved solids | ≤1200 | 681 | 674 | 686 | 655 | 647 | 645 | 550 | 621 | 615 | 625 | 694 | 641 | 471 | 458 | 508 | 467 | 428 | 510 | 525 | 452 | 448 | 575 | 595 | 575
Iron | N/A | bar: 2019-07-02 to 2020-06-23
Magnesium | N/A | 14.2 | 20.5 | 21.8 | 22 | 21.5 | 20.9 | 18.1 | 21.5 | 20.6 | 19.1 | 20.3 | 19.7 | 16.2 | <50 | 21.2 | 18.8 | 16.6 | 17.9 | 15.9 | 14.4 | 16.1 | 20.7 | 20.8 | 20
Aluminium | ≤300 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <0.5 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Redelinghuys - WTW Final
Date
| Range | 2019-07-02 | 2019-07-16 | 2019-08-13 | 2019-08-27 | 2019-09-10 | 2019-09-25 | 2019-10-08 | 2019-10-23 | 2019-11-12 | 2019-11-26 | 2019-12-11 | 2019-12-23 | 2020-01-14 | 2020-01-28 | 2020-02-11 | 2020-02-25 | 2020-03-10 | 2020-03-24 | 2020-04-07 | 2020-04-21 | 2020-05-12 | 2020-05-26 | 2020-06-09 | 2020-06-23
pH | ≤5 - ≤9.7 | 6.47 | 6.71 | 6.68 | 6.68 | 7.11 | 6.54 | 6.6 | 6.71 | 6.59 | 6.54 | 6.66 | 6.48 | 6.36 | 6.59 | 6.54 | 6.4 | 6.34 | 6.74 | 6.53 | 6.26 | 5.93 | 6.4 | 6.37 | 6.36
Conductivity | ≤170 | 99.5 | 94.6 | 96.6 | 92.1 | 107 | 90.8 | 77.9 | 94.8 | 87.4 | 90.2 | 98.6 | 81.8 | 66.7 | 64.5 | 68.7 | 62.8 | 60.9 | 72.4 | 68.5 | 69.6 | 66.9 | 89.3 | 87.4 | 84.7
Turbidity | ≤5 | <0.32 | 0.32 | <0.32 | <0.32 | <0.32 | 0.36 | <0.32 | <0.32 | <0.32 | <0.32 | 3.18 | 3.83 | 0.63 | 0.69 | 0.4 | 0.7 | 0.37 | 0.98 | 0.42 | 0.33 | <0.32 | 0.63 | <0.32 | <0.32
Colour | ≤15 | 23 | 17 | 12 | 18 | <10 | 21 | <10 | <10 | <10 | 10 | <10 | 14 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 16.3 | 15.2 | 16.1 | 16.5 | 13.9 | 14.6 | 14.4 | 17.1 | 16 | 13.8 | 14.6 | 13.6 | 10.5 | <0.50 | 12.9 | 11.6 | 10.6 | 13.8 | 9.48 | 10 | 10.5 | 14.9 | 14.9 | 14.9
Chloride | ≤300 | 223 | 214 | 211 | 212 | 242 | 202 | 187 | 215 | 217 | 211 | 230 | 194 | 153 | 157 | 158 | 145 | 136 | 176 | 150 | 157 | 152 | 210 | 196 | 206
Flouride | ≤1.5 | bar: 2019-07-02 to 2020-06-23
Dissolved solids | ≤1200 | 697 | 662 | 669 | 645 | 747 | 636 | 545 | 664 | 612 | 631 | 690 | 573 | 467 | 452 | 481 | 440 | 426 | 507 | 480 | 466 | 442 | 598 | 586 | 567
Iron | N/A | bar: 2019-07-02 to 2020-06-23
Magnesium | N/A | 14 | 20.8 | 21.6 | 22.2 | 21.1 | 20.8 | 18 | 21.2 | 20.7 | 19.4 | 23 | 20.7 | 16.2 | <0.5 | 23 | 17.7 | 14.9 | 17.8 | 14.1 | 15 | 16.1 | 21.6 | 20.7 | 19.8
Aluminium | ≤300 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected

## EK
OUR WATER MEETS THE REQUIREMENTS OF SANS 241-2:2015
Area Tested | Eendekuil - Municipal Office
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-14 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-04-08 | 2020-04-22 | 2020-05-13 | 2020-05-27 | 2020-06-10 | 2020-06-24
pH | ≤5 - ≤9.7 | 9.57 | 9.44 | 9.27 | 9.89 | 8.64 | 9.12 | 8.73 | 9.02 | 9.38 | 8.46 | 8.91 | 9.31 | 8.6 | 8.91 | 8.08 | 8.62 | 8.56 | 9.14 | 8.83 | 8.12 | 8.86 | 8.28 | 8.64 | 8.33
Conductivity | ≤170 | 11.3 | 7.14 | 9.09 | 8.55 | 5.86 | 8.22 | 7.07 | 9.29 | 9.54 | 8.65 | 8.89 | 9.39 | 9.09 | 9.04 | 10.1 | 9.98 | 8.86 | 9.16 | 9.55 | 10 | 9.85 | 22.1 | 21.4 | 23.2
Turbidity | ≤5 | 0.5 | 0.74 | 0.66 | 0.54 | 1.6 | 0.64 | 0.55 | 0.46 | 0.49 | 0.7 | 0.95 | 0.49 | 0.73 | 0.65 | 0.45 | 0.83 | 0.67 | 0.97 | 1.52 | 1.18 | 1.47 | 0.57 | 0.36 | 1.37
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 5.96 | 6.07 | 4.47 | 6.5 | 4.83 | 5.53 | 7.28 | 5.28 | 5.95 | 4.03 | 5.44 | 6.29 | 3.93 | 5.71 | 8.37 | 5.66 | 6.45 | 7.85 | 6.87 | 6.69 | 6.91 | 21.1 | 22.9 | 22.2
Chloride | ≤300 | bar: 2019-07-03 to 2020-06-24
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-24
Dissolved solids | ≤1200 | 79 | 50 | 64 | 60 | 41 | 58 | 49 | 65 | 67 | 61 | 62 | 66 | 64 | 63 | 71 | 70 | 61 | 64 | 67 | 67 | 66 | 148 | 143 | 155
Iron | N/A | bar: 2019-07-03 to 2020-06-24
Magnesium | N/A | <0.50 | <0.5 | <0.5 | 0.57 | <0.5 | <0.5 | 0.8 | <0.5 | <0.5 | 0.62 | <0.5 | 0.85 | <0.5 | <0.5 | 0.67 | 0.71 | 0.6 | <0.5 | <0.5 | <0.5 | <0.5 | 2.04 | 2.07 | 3.82
Aluminium | ≤300 | 103 | <50 | <50 | <50 | 175 | <50 | <50 | 74.3 | <50 | 79.5 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Eendekuil - WTW Final
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-14 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-04-08 | 2020-04-22 | 2020-05-13 | 2020-05-27 | 2020-06-10 | 2020-06-24
pH | ≤5 - ≤9.7 | 9.58 | 9.57 | 9.2 | 9.87 | 9.19 | 8.74 | 8.91 | 8.99 | 9.05 | 7.46 | 8.81 | 8.73 | 7.71 | 8.89 | 7.69 | 8.97 | 8.97 | 8.83 | 8.85 | 8.06 | 8.45 | 8.19 | 8.69 | 8.52
Conductivity | ≤170 | 10.7 | 7.44 | 9.43 | 7.82 | 21.3 | 7.29 | 7.22 | 7.96 | 11.2 | 6.97 | 12.9 | 9.49 | 8.82 | 8.75 | 11.5 | 10.3 | 8.92 | 9.24 | 8.97 | 9.7 | 9.54 | 21.4 | 22.8 | 24.1
Turbidity | ≤5 | 0.69 | 0.43 | 0.89 | 1.25 | 2.13 | 1.14 | 1.41 | 1.41 | 1.99 | 2.55 | 2.87 | 1.76 | 0.89 | 1.13 | 1.34 | 2.32 | 0.85 | 1.55 | 2.49 | 1.2 | 2.1 | 1.26 | 1.26 | 0.39
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 5.76 | 6.87 | 4.37 | 6.39 | 4.58 | 4.89 | 7.73 | 5.39 | 5.46 | 3.65 | 5.46 | 5.4 | 2.69 | 5.45 | 9.59 | 5.4 | 7.16 | 7.08 | 6.79 | 6.22 | 5.62 | 21.8 | 24.2 | 23.7
Chloride | ≤300 | 18.3 | 11 | 16.8 | 10.4 | 51.8 | 11.9 | 11 | 12.9 | 19.8 | 12 | - | 18.4 | 17.9 | 17 | 16.5 | 20.6 | 15.5 | 17.4 | 14.7 | 17.6 | 19.1 | 20.6 | 18.2 | 24
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-24
Dissolved solids | ≤1200 | 75 | 52 | 66 | 55 | 149 | 51 | 51 | 56 | 78 | 49 | 90 | 66 | 62 | 61 | 81 | 72 | 62 | 65 | 63 | 55 | 64 | 143 | 153 | 161
Iron | N/A | bar: 2019-07-03 to 2020-06-24
Magnesium | N/A | <0.5 | <0.5 | <0.5 | 0.61 | <50 | <0.50 | 0.76 | <0.5 | <0.5 | 0.56 | <0.5 | <0.5 | <0.5 | <0.5 | 0.68 | 0.52 | 0.55 | <0.5 | <0.5 | <0.5 | <0.5 | 2.16 | 2.14 | 3.89
Aluminium | ≤300 | 85.7 | 95.7 | 63.7 | <50 | 161 | <50 | <50 | 79.7 | <50 | 99.3 | 56.1 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | 7 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected

## PB
OUR WATER MEETS THE REQUIREMENTS OF SANS 241-2:2015
Area Tested | Piketberg - Community Centre
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-15 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-04-08 | 2020-04-22 | 2020-06-25
pH | ≤5 - ≤9.7 | 7.05 | 7.04 | 5.89 | 6.46 | 6.51 | 6.87 | 6.84 | 6.99 | 4.78 | 6.66 | 9.66 | 7.27 | 7.38 | 7.15 | 7.27 | 7.43 | 6.84 | 7.22 | 9.39 | 7.86 | 9.82
Conductivity | ≤170 | 34.8 | 31.2 | 35 | 38.5 | 43.9 | 51.6 | 56 | 60 | 22.7 | 30.7 | 28.9 | 32.6 | 28.4 | 25.8 | 25 | 22.7 | 21.2 | 21.1 | 22.8 | 23.1 | 26.1
Turbidity | ≤5 | 1.66 | 28.2 | 3.03 | 2.29 | 0.34 | 0.42 | 0.32 | 0.33 | 0.48 | 0.41 | 0.66 | 0.76 | 0.35 | 0.41 | <0.32 | <0.32 | <0.32 | 0.71 | 0.5 | 8.07 | 3.64
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 12.4 | 12.6 | 12.8 | 13.8 | 13.8 | 16.1 | 21.6 | 17.4 | 6.97 | 9 | 9.29 | 12.9 | 7.79 | 9.83 | 10.2 | 8.17 | 7.5 | 10 | 7.45 | 12.8 | 2.86
Chloride | ≤300 | bar: 2019-07-03 to 2020-06-25
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-25
Dissolved solids | ≤1200 | 244 | 218 | 245 | 270 | 307 | 361 | 392 | 420 | 159 | 215 | 202 | 228 | 199 | 181 | 175 | 159 | 148 | 148 | 160 | 155 | 176
Iron | N/A | bar: 2019-07-03 to 2020-06-25
Magnesium | N/A | 6.52 | 5.37 | 6.6 | 7.79 | 9 | 11.1 | 13.7 | 13 | 4.24 | 6.12 | 8.48 | 7.99 | 2.27 | 6.15 | 5.86 | 5.5 | 6.09 | 4.73 | 5.71 | 2.46 | 1.96
Aluminium | ≤300 | <50 | 57.1 | <50 | <50 | 78.3 | <50 | <50 | 70.5 | 76.3 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 179 | 215 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Piketberg - WTW Final
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-15 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-04-08 | 2020-04-22 | 2020-05-13 | 2020-05-27 | 2020-06-10 | 2020-06-25
pH | ≤5 - ≤9.7 | 5.42 | 6.17 | 4.72 | 4.59 | 5.86 | 6.62 | 6.31 | 6.33 | 4.46 | 6.04 | 7.03 | 6.82 | 6.84 | 6.75 | 6.73 | 6.79 | 6.78 | 6.69 | 6.5 | 9.7 | 7.23 | 6.59 | 6.66 | 6.21
Conductivity | ≤170 | 27.8 | 27.4 | 32.6 | 37.3 | 58.5 | 52.4 | 60.7 | 60.7 | 22.7 | 25.4 | 28.8 | 32.3 | 26.7 | 25 | 23.1 | 21.4 | 21.2 | 21 | 20.4 | 24 | 26.6 | 40.2 | 26.9 | 28.1
Turbidity | ≤1 | 18.6 | 2.27 | 3.99 | 8.09 | 1.46 | 1.18 | 0.4 | 1.24 | 3.6 | 7.47 | 0.76 | 3.3 | 1.73 | 0.88 | 2.16 | 0.56 | 0.69 | 2.19 | 5.88 | 3.94 | 1.18 | 9.96 | 3.04 | 3.35
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 6.04 | 7.47 | 7.27 | 9.01 | 13.4 | 14.8 | 19.4 | 16.1 | 5.84 | 6.36 | 9.96 | 10.7 | 6.69 | 8.5 | 7.58 | 6.47 | 8.39 | 7 | 5.44 | 13.9 | 10.5 | 10.5 | 7.68 | 8.59
Chloride | ≤300 | 55.3 | 56.1 | 70.3 | 75.6 | 134 | 121 | 140 | 135 | 35.4 | 49.9 | 55.9 | 72.7 | 58.1 | 53.2 | 45.9 | 42.7 | 38 | 44.4 | 42.1 | 36.2 | 57.9 | 99 | 54.4 | 58.3
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-25
Dissolved solids | ≤1200 | 195 | 192 | 228 | 261 | 410 | 367 | 425 | 425 | 159 | 178 | 202 | 226 | 187 | 175 | 162 | 150 | 148 | 147 | 143 | 161 | 178 | 269 | 180 | 188
Iron | N/A | bar: 2019-07-03 to 2019-12-24; 2020-01-29 to 2020-06-25
Magnesium | N/A | 5.67 | 5.07 | 6.08 | 7.13 | 12.6 | 11.5 | 15.7 | 13.4 | 3.8 | 5.22 | 6.28 | 8.2 | - | 5.27 | 5.62 | 5.16 | 6.02 | 4.83 | 4.62 | 3.85 | 6.03 | 10.4 | 6.27 | 6.59
Aluminium | ≤300 | 136 | 55.5 | 1047 | <50 | 150 | <50 | <50 | 67.5 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 68 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Piketberg - Elektriesstoor
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-15 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-04-08 | 2020-04-22 | 2020-05-27 | 2020-06-25
pH | ≤5 - ≤9.7 | 7.18 | 7.2 | 6.26 | 6.87 | 7.14 | 7.26 | 7.21 | 7.26 | 6.49 | 7.2 | 7.36 | 7.45 | 7.33 | 7.42 | 7.23 | 6.84 | 6.91 | 7.17 | 7.2 | 6.83
Conductivity | ≤170 | 32.1 | 30.9 | 34.1 | 35.5 | 45.8 | 47.8 | 50.2 | 54.8 | 23.2 | 31.9 | 28.3 | 26.3 | 24.3 | 22.8 | 22 | 20.6 | 20.3 | 21.1 | 35.3 | 27.3
Turbidity | ≤5 | 0.46 | 1.38 | 3.6 | 1.54 | <0.32 | 0.62 | <0.32 | <0.32 | 1.46 | 0.63 | 0.38 | <0.32 | <0.32 | <0.32 | <0.32 | 0.33 | 0.38 | 0.48 | 0.41 | 1.21
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 15.8 | 13.2 | 13.7 | 19.9 | 20.1 | 21.2 | 24.7 | 24 | 11.2 | 14.1 | 10.9 | 13.4 | 10.6 | 9.62 | 10.4 | 7.89 | 7.53 | 10.5 | 12.3 | 10.1
Chloride | ≤300 | bar: 2019-07-03 to 2020-06-25
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-25
Dissolved solids | ≤1200 | 225 | 216 | 23.9 | 249 | 321 | 335 | 351 | 384 | 162 | 223 | 198 | 184 | 170 | 160 | 164 | 144 | 142 | 141 | 237 | 183
Iron | N/A | bar: 2019-07-03 to 2020-06-25
Magnesium | N/A | 5.87 | 5.37 | 6.22 | 6.53 | 8.99 | 9.31 | 10.7 | 11.2 | 4.07 | 5.75 | 2.76 | 5.3 | 5.66 | 5.17 | 4.88 | 4.57 | 4.22 | 3.78 | 9.13 | 6.48
Aluminium | ≤300 | 51.3 | 62.9 | <50 | <50 | 193 | <50 | <50 | 50.5 | <50 | 90.9 | <50 | 52.9 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Piketberg - Municipal offices
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-15 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-04-08 | 2020-04-22 | 2020-05-13 | 2020-05-27 | 2020-06-10 | 2020-06-25
pH | ≤5 - ≤9.7 | 7.14 | 7.41 | 6.84 | 6.83 | 6.97 | 7.04 | 7.04 | 7.18 | 5.98 | 7.1 | 7.69 | 7.32 | 7.24 | 7.36 | 7.17 | 7.23 | 7.13 | 6.89 | 7.04 | 7.4 | 7.09 | 7.06 | 7.26 | 6.75
Conductivity | ≤170 | 31.9 | 31.2 | 33.8 | 35.5 | 46.4 | 49.2 | 53.7 | 57.4 | 22.5 | 28.2 | 30 | 32.8 | 28.2 | 26 | 24.4 | 22.8 | 21.6 | 20.3 | 20.7 | 21.6 | 26.1 | 35.2 | 28.3 | 27.3
Turbidity | ≤5 | 1.5 | 1.59 | 4.55 | 3.41 | 0.95 | 0.9 | 0.71 | 0.42 | 2.57 | 0.53 | 1.26 | 0.55 | 0.68 | 0.47 | 0.38 | 0.61 | <0.32 | 0.53 | 0.55 | 0.47 | 0.89 | 0.62 | 1.79 | 2.91
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 16.4 | 19.1 | 18.4 | 19.1 | 18.8 | 18.1 | 21.8 | 20.5 | 9.91 | 10.7 | 16.2 | 13.6 | 11.9 | 13 | 11.3 | 9.54 | 9.48 | 7.4 | 7 | 11.5 | 9.84 | 11.9 | 13.1 | 10.5
Chloride | ≤300 | bar: 2019-07-03 to 2020-06-25
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-25
Dissolved solids | ≤1200 | 223 | 218 | 237 | 249 | 325 | 344 | 376 | 402 | 158 | 197 | 210 | 230 | 197 | 182 | 171 | 160 | 161 | 142 | 145 | 146 | 175 | 236 | 190 | 183
Iron | N/A | bar: 2019-07-03 to 2020-06-25
Magnesium | N/A | 5.84 | 5.18 | 5.71 | 6.82 | 9.42 | 10.1 | 12.2 | 12 | 4.14 | 5.33 | 5.74 | 7.93 | 3.29 | 5.13 | 5.69 | 5.2 | 6.07 | 4.69 | 4.32 | 3.95 | 5.82 | 9 | 5.96 | 6.48
Aluminium | ≤300 | <50 | 77.4 | <50 | <50 | 109 | <50 | <50 | 72.5 | <50 | 62.8 | 470 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 67.5 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected

## AU
OUR WATER MEETS THE REQUIREMENTS OF SANS 241-2:2015
Area Tested | Aurora - Municipal office
Date
| Range | 2019-07-02 | 2019-07-16 | 2019-08-13 | 2019-08-27 | 2019-09-10 | 2019-09-25 | 2019-10-08 | 2019-10-23 | 2019-11-12 | 2019-11-26 | 2019-12-10 | 2019-12-23 | 2020-01-14 | 2020-01-28 | 2020-02-11 | 2020-02-25 | 2020-03-10 | 2020-03-24 | 2020-04-07 | 2020-04-22 | 2020-05-12 | 2020-05-26 | 2020-06-09 | 2020-06-23
pH | ≤5 - ≤9.7 | 7.68 | 8.5 | 7.05 | 7.31 | 7.09 | 7.4 | 7.36 | 7.57 | 7.77 | 7.77 | 7.86 | 7.6 | 8.65 | 8.41 | 8.24 | 7.3 | 7.55 | 6.79 | 7.31 | 7.28 | 6.97 | 7.03 | 6.98 | 6.94
Conductivity | ≤170 | 159 | 153 | 140 | 149 | 143 | 135 | 141 | 145 | 145 | 150 | 146 | 140 | 144 | 140 | 143 | 158 | 145 | 131 | 152 | 150 | 150 | 148 | 152 | 148
Turbidity | ≤5 | <0.32 | 0.34 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | 1.39 | <0.32 | <0.32 | <0.32 | <0.32 | 0.36 | 0.35 | 0.36 | <0.32 | 0.35 | 0.43 | <0.32 | 0.41 | <0.32 | 0.32 | <0.32
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 21.6 | 22.6 | 21.7 | 24 | 21.1 | 18.1 | 21.4 | 24.4 | 24.4 | 23.2 | 23.8 | 22.7 | 21.7 | <0.5 | 22.9 | 25.8 | 20.7 | 17.8 | 17.8 | 19.3 | 17.8 | 16.9 | 20.7 | 19.8
Chloride | ≤300 | bar: 2019-07-02 to 2020-06-23
Flouride | ≤1.5 | bar: 2019-07-02 to 2020-06-23
Dissolved solids | ≤1200 | 1111 | 1072 | 979 | 1044 | 999 | 946 | 984 | 1013 | 1016 | 1049 | 1022 | 979 | 1007 | 981 | 1002 | 1109 | 1020 | 916 | 1066 | 1007 | 1008 | 994 | 1021 | 990
Iron | N/A | bar: 2019-07-02 to 2020-06-23
Magnesium | N/A | 20.4 | 34.3 | 32.4 | 36.9 | 35.9 | 30.7 | 32.9 | 36.1 | 35.6 | 33.3 | 36.9 | 36.9 | 35.9 | <0.5 | 47.7 | 52.6 | 37.7 | 33.2 | 34.8 | 34.9 | 40 | 37.4 | 38.7 | 36.8
Aluminium | ≤300 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Aurora - WTW Final
Date
| Range | 2019-07-02 | 2019-07-16 | 2019-08-13 | 2019-08-27 | 2019-09-10 | 2019-09-25 | 2019-10-08 | 2019-10-23 | 2019-11-12 | 2019-11-26 | 2019-12-10 | 2019-12-23 | 2020-01-14 | 2020-01-28 | 2020-02-11 | 2020-02-25 | 2020-03-10 | 2020-03-24 | 2020-04-07 | 2020-04-22 | 2020-05-12 | 2020-05-26 | 2020-06-09 | 2020-06-23
pH | ≤5 - ≤9.7 | 6.33 | 6.39 | 6.41 | 6.6 | 6.37 | 6.21 | 6.3 | 6.46 | 6.31 | 6.28 | 6.39 | 6.34 | 6.28 | 6.46 | 6.53 | 6.65 | 6.26 | 6.24 | 6.33 | 6.44 | 6.19 | 6.45 | 6.46 | 6.29
Conductivity | ≤170 | 154 | 149 | 133 | 137 | 130 | 141 | 142 | 144 | 148 | 147 | 146 | 133 | 144 | 141 | 141 | 156 | 142 | 139 | 161 | 152 | 150 | 140 | 145 | 147
Turbidity | ≤5 | <0.32 | <0.32 | 0.33 | 0.51 | 0.36 | 0.72 | <0.32 | 0.49 | <0.32 | 0.39 | 0.48 | <0.32 | <0.32 | <0.32 | <0.32 | 0.69 | 0.66 | 1.73 | <0.32 | 0.4 | 0.53 | 0.48 | 0.35 | <0.32
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 17.8 | 16 | 19.2 | 20.5 | 15.7 | 13 | 16 | 18 | 17.4 | 16 | 16.9 | 19.1 | 15.2 | <0.5 | 15 | 19.2 | 16.4 | 16.9 | 13 | 14.9 | 14.3 | 16.6 | 17.6 | 16.7
Chloride | ≤300 | bar: 2019-07-02 to 2020-06-23
Flouride | ≤1.5 | bar: 2019-07-02 to 2020-06-23
Dissolved solids | ≤1200 | 1075 | 1041 | 932 | 958 | 911 | 986 | 995 | 1005 | 1037 | 1027 | 1021 | 928 | 1005 | 987 | 984 | 1093 | 994 | 976 | 1066 | 1020 | 1004 | 940 | 972 | 984
Iron | N/A | bar: 2019-07-02 to 2020-06-23
Magnesium | N/A | 21.3 | 34.4 | 30.4 | 33.6 | 31.9 | 33.5 | 35.1 | 36.5 | 38 | 33.3 | 37.6 | 36 | 38.3 | <0.5 | 47.4 | 54 | 37.3 | 36 | 36.2 | 37.1 | 40.4 | 30.7 | 37.6 | 37.5
Aluminium | ≤300 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected

## VD
OUR WATER MEETS THE REQUIREMENTS OF SANS 241-2:2015
Area Tested | Velddrif - Civic centre
Date
| Range | 2019-07-02 | 2019-07-16 | 2019-08-13 | 2019-08-27 | 2019-09-10 | 2019-09-25 | 2019-10-08 | 2019-10-23 | 2019-11-12 | 2019-11-26 | 2019-12-10 | 2019-12-23 | 2020-01-14 | 2020-01-28 | 2020-02-11 | 2020-02-25 | 2020-03-10 | 2020-03-24 | 2020-04-21
pH | ≤5 - ≤9.7 | 8.95 | 9.18 | 8.37 | 7.68 | 7.7 | 8.28 | 7.81 | 9.41 | 7.98 | 7.58 | 9.63 | 8.69 | 8.69 | 8.58 | 8.82 | 8.98 | 8.29 | 8.78 | 9.94
Conductivity | ≤170 | 33.7 | 34.3 | 35.2 | 42 | 43.2 | 56 | 52.2 | 51.7 | 42.7 | 25 | 27.8 | 31.2 | 32 | 29.1 | 27.9 | 25.1 | 26 | 24.6 | 21.9
Turbidity | ≤5 | 0.52 | 0.33 | 0.79 | <0.32 | <0.32 | 0.35 | <0.32 | 0.32 | <0.32 | <0.32 | 0.41 | <0.32 | <0.32 | <0.32 | 0.33 | <0.32 | <0.32 | <0.32 | 0.42
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 15.7 | 14 | 14.9 | 14.9 | 15.8 | 19.2 | 18.1 | 18.9 | 17.5 | 12.2 | 16.9 | 17.4 | 17.5 | 17.6 | 20.3 | 14.7 | 16.9 | 14.2 | 11.7
Chloride | ≤300 | bar: 2019-07-02 to 2020-04-21
Flouride | ≤1.5 | bar: 2019-07-02 to 2020-04-21
Dissolved solids | ≤1200 | 236 | 240 | 246 | 294 | 302 | 392 | 368 | 362 | 299 | 175 | 196 | 218 | 224 | 204 | 195 | 176 | 182 | 172 | 147
Iron | N/A | bar: 2019-07-02 to 2020-04-21
Magnesium | N/A | 5.8 | 6.01 | 5.9 | 8.12 | 8.28 | 11 | 10.6 | 10.3 | 8.85 | 4.28 | 5.02 | 5.2 | 6.36 | 5.5 | 6.02 | 4.56 | 4.85 | 4.27 | 3.2
Aluminium | ≤300 | 74.7 | 59 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 63.4 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Velddrif - Municipal Office
Date
| Range | 2019-07-02 | 2019-07-16 | 2019-08-13 | 2019-08-27 | 2019-09-10 | 2019-09-25 | 2019-10-08 | 2019-10-23 | 2019-11-12 | 2019-11-26 | 2019-12-10 | 2019-12-23 | 2020-01-14 | 2020-01-28 | 2020-02-11 | 2020-02-25 | 2020-03-10 | 2020-03-24 | 2020-04-07 | 2020-04-21 | 2020-05-12 | 2020-05-26 | 2020-06-10 | 2020-06-23
pH | ≤5 - ≤9.7 | 8.42 | 8.64 | 8.32 | 7.96 | 7.5 | 7.76 | 7.53 | 7.88 | 7.6 | 7.95 | 7.71 | 8.17 | 8 | 8.29 | 8.11 | 8.69 | 8.47 | 8.6 | 8.86 | 9.14 | 8.74 | 8.77 | 9.13 | 8.96
Conductivity | ≤170 | 34.2 | 34.5 | 35.2 | 41.3 | 42.9 | 55.8 | 53.2 | 54.6 | 40.4 | 26.8 | 30.6 | 30.7 | 32 | 29.9 | 27.1 | 25.1 | 26.7 | 26.2 | 24.9 | 23.8 | 21 | 21.6 | 23.3 | 26.7
Turbidity | ≤5 | <0.32 | 0.36 | 0.34 | 0.32 | <0.32 | <0.32 | 0.44 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | 0.44 | 0.55 | 0.8 | 0.42 | <0.32
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 16.4 | 14.4 | 15.4 | 15.5 | 14.7 | 15.9 | 19 | 21.8 | 16.6 | 13.8 | 16.7 | 17 | 17.6 | 18.9 | 18.7 | 18.5 | 16.4 | 15 | 14.2 | 16.9 | 14.3 | 13.3 | 14.1 | 16.1
Chloride | ≤300 | bar: 2019-07-02 to 2020-06-23
Flouride | ≤1.5 | bar: 2019-07-02 to 2020-06-23
Dissolved solids | ≤1200 | 239 | 242 | 246 | 289 | 300 | 391 | 372 | 382 | 283 | 188 | 214 | 216 | 224 | 209 | 190 | 176 | 187 | 176 | 174 | 159 | 141 | 145 | 155 | 172
Iron | N/A | bar: 2019-07-02 to 2020-06-23
Magnesium | N/A | 3.81 | 5.87 | 5.74 | 7.77 | 7.94 | 10.7 | 10.5 | 11.2 | 8.48 | 4.48 | 5.58 | 6.11 | 6.49 | 5.73 | 6.14 | 5.94 | 5.01 | 4.31 | 3.89 | 3.69 | 3.85 | 4.39 | 4.08 | 6.2
Aluminium | ≤300 | 93.5 | 80.6 | <50 | <50 | 59.9 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 80.5 | <50 | <50 | <50 | 94 | 96.7 | 78.4 | 96.4 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Velddrif - WTW Final/Reservoir
Date
| Range | 2019-07-02 | 2019-07-16 | 2019-08-13 | 2019-08-27 | 2019-09-10 | 2019-09-25 | 2019-10-08 | 2019-10-23 | 2019-11-12 | 2019-11-26 | 2019-12-10 | 2019-12-23 | 2020-01-14 | 2020-01-28 | 2020-02-11 | 2020-02-25 | 2020-03-10 | 2020-03-24 | 2020-04-07 | 2020-04-21 | 2020-05-12 | 2020-05-26 | 2020-06-10 | 2020-06-23
pH | ≤5 - ≤9.7 | 8.32 | 8.38 | 7.65 | 7.62 | 7.43 | 7.45 | 7.53 | 7.51 | 7.35 | 7.49 | 7.52 | 7.72 | 7.81 | 7.7 | 7.63 | 7.9 | 7.63 | 7.7 | 7.72 | 7.95 | 8.61 | 8.49 | 8.57 | 8.14
Conductivity | ≤170 | 35.2 | 34.6 | 36.3 | 41.1 | 46.3 | 54.2 | 53.7 | 52.6 | 33.2 | 23.6 | 26.7 | 31.6 | 31.3 | 28.3 | 25.3 | 23 | 25 | 25 | 22.2 | 21.5 | 19.9 | 21.1 | 22.3 | 26.7
Turbidity | ≤5 | 0.87 | <0.32 | 0.57 | 1.22 | <0.32 | 0.65 | 0.42 | 0.33 | <0.32 | <0.32 | <0.32 | 0.61 | <0.32 | <0.32 | <0.32 | 0.43 | <0.32 | 0.36 | 1.31 | <0.32 | <0.32 | <0.32 | 0.39 | <0.32
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 15.4 | 12.8 | 13.8 | 14 | 14.7 | 15.3 | 18.8 | 19.9 | 14.3 | 11.3 | 13.2 | 16.1 | 16.4 | 17.4 | 14.6 | 15.1 | 14.9 | 14.2 | 10.8 | 12.1 | 12.5 | 12.1 | 12 | 13.8
Chloride | ≤300 | bar: 2019-07-02 to 2020-06-23
Flouride | ≤1.5 | bar: 2019-07-02 to 2020-06-23
Dissolved solids | ≤1200 | 246 | 242 | 254 | 288 | 324 | 379 | 376 | 368 | 232 | 165 | 180 | 221 | 219 | 198 | 177 | 161 | 175 | 176 | 155 | 144 | 133 | 141 | 149 | 179
Iron | N/A | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | - | - | - | - | - | - | - | <20
Magnesium | N/A | 3.95 | 5.86 | 6.04 | 7.9 | 8.58 | 10.6 | 11.2 | 11.3 | 6.84 | 4 | 4.89 | 6.63 | 6.28 | 5.77 | 5.27 | 5.8 | 4.73 | 4.29 | 3.92 | 3.74 | 3.74 | 4.41 | 4.31 | 6.46
Aluminium | ≤300 | 69.4 | 71.5 | <50 | <50 | 55.1 | <50 | <50 | <50 | <50 | <50 | <50 | 60.6 | <50 | <50 | 60.5 | 63.5 | <50 | <50 | <50 | 92.5 | 154 | 160 | 96.6 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected

## PV
OUR WATER MEETS THE REQUIREMENTS OF SANS 241-2:2015
Area Tested | Porterville - Municipal office
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-14 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-04-08 | 2020-04-22 | 2020-05-13 | 2020-05-27 | 2020-06-10 | 2020-06-24
pH | ≤5 - ≤9.7 | 9.22 | 9.2 | 8.5 | 6.81 | 8.21 | 7.68 | 8.33 | 7.79 | 7.33 | 7.15 | 8.33 | 8.09 | 7.47 | 7.81 | 8.28 | 8.24 | 8.66 | 8.74 | 8.68 | 8.71 | 8.87 | 9.27 | 9.61 | 9.68
Conductivity | ≤170 | 9.55 | 8.73 | 7.75 | 6.67 | 7.93 | 7.94 | 7.84 | 7.61 | 7.49 | 7.81 | 7.83 | 7.78 | 7.62 | 8.4 | 8.43 | 8 | 8.49 | 7.09 | 8.92 | 9.24 | 9.13 | 9.79 | 11.2 | 10.8
Turbidity | ≤5 | 0.39 | 0.53 | 0.45 | 0.44 | 0.37 | 0.58 | 0.47 | 0.46 | 0.75 | 0.7 | 0.47 | 0.44 | 0.5 | 0.41 | 0.4 | 1.22 | 0.7 | <0.32 | 0.45 | 0.66 | <0.32 | 0.58 | 0.63 | 0.69
Colour | ≤15 | bar: 2019-07-03 to 2020-06-24
Calcium | N/A | 8.3 | 8.4 | 6.08 | 8.53 | 6.98 | 7.33 | 9.22 | 6.68 | 5.96 | 6.01 | 7.4 | 7.68 | 6.57 | 9.12 | 8.61 | 7.94 | 8.69 | 7.33 | 8.14 | 8.95 | 9.81 | 9.36 | 11.3 | 11.6
Chloride | ≤300 | bar: 2019-07-03 to 2020-06-24
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-24
Dissolved solids | ≤1200 | bar: 2019-07-03 to 2020-06-24
Iron | N/A | bar: 2019-07-03 to 2020-06-24
Magnesium | N/A | 0.91 | 0.95 | 0.96 | 1.32 | 1.04 | 1.04 | 1.4 | 1.03 | 0.96 | 1.19 | 0.83 | 1.21 | <0.5 | 1.1 | 0.94 | 1.15 | 1.2 | <0.5 | 0.98 | 1.07 | 0.85 | 1.17 | 0.96 | 2.76
Aluminium | ≤300 | 108 | 96.9 | 55.7 | <50 | <50 | <50 | <50 | 106 | <50 | 97.4 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 137 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Porterville - Library
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-14 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-06-24
pH | ≤5 - ≤9.7 | 9.89 | 9.1 | 7.88 | 7.22 | 8.86 | 7.75 | 8.73 | 7.52 | 7.63 | 7.34 | 8.61 | 8.38 | 7.67 | 8.77 | 8.3 | 8.02 | 8.6 | 9.25 | 9.7
Conductivity | ≤170 | 11.6 | 8.91 | 7.93 | 7.27 | 8.54 | 7.7 | 8.19 | 7.74 | 7.46 | 8.05 | 7.95 | 8.21 | 7.52 | 9.06 | 8.35 | 8.1 | 8.64 | 7.83 | 10.7
Turbidity | ≤5 | 0.56 | 70.2 | 0.46 | 0.48 | 0.44 | 0.64 | 0.44 | 0.45 | 0.55 | 0.5 | 0.61 | 0.61 | 0.5 | 0.94 | 0.56 | 0.53 | 0.42 | 0.72 | 0.4
Colour | ≤15 | bar: 2019-07-03 to 2020-06-24
Calcium | N/A | 11.4 | 8.74 | 6.19 | 5.66 | 8.04 | 7.39 | 9.57 | 6.84 | 6.3 | 6.48 | 7.33 | 9.17 | 7.56 | 11.3 | 8.92 | 7.93 | 8.74 | 8.43 | 12
Chloride | ≤300 | bar: 2019-07-03 to 2020-06-24
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-24
Dissolved solids | ≤1200 | bar: 2019-07-03 to 2020-06-24
Iron | N/A | bar: 2019-07-03 to 2020-06-24
Magnesium | N/A | 0.97 | 0.94 | 0.97 | 1.3 | 1.03 | 1.12 | 1.42 | 1.03 | 0.91 | 1.14 | 0.91 | 1.23 | <0.5 | 0.9 | 0.96 | 1.19 | 1.17 | 0.62 | 2.74
Aluminium | ≤300 | <50 | 85.3 | 51.9 | <50 | <50 | <50 | <50 | <50 | <50 | 83.6 | <50 | <50 | <50 | 68.9 | <50 | <50 | <50 | <50 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
Area Tested | Porterville - WWTW Tap
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-14 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-03-26 | 2020-04-08 | 2020-04-22 | 2020-05-13 | 2020-05-27 | 2020-06-10 | 2020-06-24
pH | ≤5 - ≤9.7 | 9.81 | 9.33 | 7.16 | 7.35 | 8.59 | 7.15 | 8.61 | 8.34 | 8.66 | 7.18 | 8.84 | 9.2 | 7.73 | 9 | 8.35 | 8.3 | 8.72 | 9.66 | 8.12 | 9.11 | 9.22 | 9.21 | 9.71 | 9.88
Conductivity | ≤170 | 11.5 | 9.31 | 7.63 | 7.27 | 8.55 | 7.48 | 8.02 | 7.95 | 8.01 | 8.02 | 8.22 | 8.86 | 7.63 | 9.06 | 8.38 | 8.05 | 8.79 | 8.78 | 8.76 | 9.67 | 9.86 | 10.1 | 11.7 | 11.2
Turbidity | ≤5 | 0.55 | 0.54 | 0.41 | 0.36 | 0.4 | 0.44 | 0.39 | 0.39 | 0.57 | 0.65 | 0.63 | 0.41 | 0.39 | 0.6 | 0.47 | 0.41 | 0.37 | 0.66 | 0.57 | 0.81 | 0.45 | 2.58 | 0.54 | 0.4
Colour | ≤15 | bar: 2019-07-03 to 2020-06-24
Calcium | N/A | 11.5 | 9.35 | 5.6 | 6.1 | 8.11 | 6.52 | 9.55 | 7.38 | 7.06 | 7.09 | 8.08 | 10.2 | 6.74 | 10.8 | 8.59 | 7.74 | 9.1 | 9.43 | 8.13 | 9.79 | 11.3 | 9.67 | 12.6 | 12.2
Chloride | ≤300 | bar: 2019-07-03 to 2020-06-24
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-24
Dissolved solids | ≤1200 | bar: 2019-07-03 to 2020-06-24
Iron | N/A | bar: 2019-07-03 to 2020-06-24
Magnesium | N/A | 0.96 | 0.91 | 0.89 | 1.24 | 0.98 | 0.97 | 1.26 | 0.89 | 0.89 | 1.08 | 0.85 | 1.14 | <0.5 | 0.8 | 0.87 | 1.14 | 1.18 | 0.69 | 0.99 | 0.98 | 0.88 | 1.12 | 1.01 | 2.76
Aluminium | ≤300 | 97.4 | 101 | <50 | <50 | <50 | <50 | <50 | 93.8 | <50 | 89.5 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 51.3 | <50 | 93 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected
.
Area Tested | Porterville - WTW Final
Date
| Range | 2019-07-03 | 2019-07-17 | 2019-08-14 | 2019-08-28 | 2019-09-11 | 2019-09-26 | 2019-10-09 | 2019-10-24 | 2019-11-14 | 2019-11-27 | 2019-12-11 | 2019-12-24 | 2020-01-16 | 2020-01-29 | 2020-02-12 | 2020-02-26 | 2020-03-11 | 2020-04-08 | 2020-04-22 | 2020-05-13 | 2020-05-27 | 2020-06-10 | 2020-06-24
pH | ≤5 - ≤9.7 | 9.4 | 8.69 | 9.24 | 6.65 | 7.17 | 7.23 | 7.48 | 6.89 | 6.68 | 6.95 | 8.21 | 9.18 | 6.39 | 7.63 | 6.97 | 7.05 | 8.18 | 8.06 | 7.75 | 8.59 | 7.47 | 9.41 | 9.43
Conductivity | ≤170 | 9.54 | 8.38 | 8.7 | 6.33 | 7.34 | 7.76 | 7.45 | 6.92 | 6.89 | 7.39 | 7.85 | 8.32 | 6.68 | 8.15 | 7.31 | 7.11 | 8.21 | 8.42 | 8.66 | 8.44 | 8.81 | 10.4 | 9.89
Turbidity | ≤5 | 1.08 | 0.44 | 0.65 | 0.52 | 0.72 | 1.05 | 0.69 | 0.56 | 0.78 | 0.93 | 0.73 | 0.9 | 0.96 | 0.66 | 0.75 | 2.43 | 0.93 | 0.6 | 0.9 | 0.7 | 1.18 | 2.84 | 0.78
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 8.14 | 7.64 | 7.48 | 4.35 | 5.9 | 6.96 | 8.64 | 5.33 | 4.77 | 5.16 | 6.99 | 8.96 | 3.53 | 8.84 | 6.23 | 5.69 | 8.08 | 7.22 | 8.04 | 8.34 | 7.55 | 10.2 | 10.6
Chloride | ≤300 | bar: 2019-07-03 to 2020-06-24
Flouride | ≤1.5 | bar: 2019-07-03 to 2020-06-24
Dissolved solids | ≤1200 | 67 | 59 | 61 | 44 | 51 | 54 | 52 | 48 | 48 | 52 | 55 | 58 | 47 | 57 | 51 | 50 | 57 | 69 | 58 | 57 | 59 | 69 | 66
Iron | N/A | bar: 2019-07-03 to 2020-06-24
Magnesium | N/A | 1.09 | 1 | 0.99 | 1.25 | 1.07 | 1.07 | 1.48 | 1.04 | 0.97 | 1.3 | 1 | 1.26 | <0.5 | 0.79 | 1 | 1.17 | 1.25 | 1.04 | 1.04 | 0.96 | 1.26 | 1.01 | 2.83
Aluminium | ≤300 | 124 | 85.5 | 53.2 | <50 | <50 | <50 | <50 | 64 | <50 | 84.8 | <50 | 50.6 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 188 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected

## DKB
OUR WATER MEETS THE REQUIREMENTS OF SANS 241-2:2015
Area Tested | Dwarskersbos - Reservoir
Date
| Range | 2019-07-02 | 2019-07-16 | 2019-08-13 | 2019-08-27 | 2019-09-10 | 2019-09-25 | 2019-10-08 | 2019-10-23 | 2019-11-12 | 2019-11-26 | 2019-12-10 | 2019-12-23 | 2020-01-14 | 2020-01-28 | 2020-02-11 | 2020-02-26 | 2020-03-10 | 2020-03-24 | 2020-04-07 | 2020-04-21 | 2020-05-12 | 2020-05-26 | 2020-06-09 | 2020-06-23
pH | ≤5 - ≤9.7 | 8.5 | 8.84 | 8.05 | 8.06 | 7.65 | 7.97 | 7.98 | 7.87 | 7.76 | 7.89 | 7.84 | 8 | 8.1 | 8 | 8.46 | 8.36 | 8.16 | 8.24 | 8.22 | 8.62 | 8.58 | 8.74 | 8.87 | 8.77
Conductivity | ≤170 | 34.3 | 34.1 | 35.1 | 41 | 43.4 | 55.7 | 52.6 | 54.5 | 46.3 | 26.2 | 26.2 | 30.4 | 32 | 28.7 | 26.2 | 25.1 | 25.6 | 23.6 | 23.2 | 22.5 | 20.6 | 21.2 | 23.4 | 26.4
Turbidity | ≤5 | 0.54 | <0.32 | 0.58 | <0.32 | <0.32 | <0.32 | 0.34 | 7.87 | <0.32 | <0.32 | <0.32 | 3.47 | <0.32 | <0.32 | <0.32 | 0.35 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32 | <0.32
Colour | ≤15 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10 | <10
Calcium | N/A | 16.6 | 14.6 | 14.9 | 15.2 | 14.8 | 19.5 | 19.9 | 21.5 | 18.7 | 14.3 | 14.5 | 18.3 | 17.5 | 18.5 | 16 | 14.8 | 15.8 | 14.3 | 13.4 | 14 | 14.9 | 13.1 | 13.7 | 15
Chloride | ≤300 | bar: 2019-07-02 to 2020-06-23
Flouride | ≤1.5 | bar: 2019-07-02 to 2020-06-23
Dissolved solids | ≤1200 | 240 | 239 | 246 | 287 | 304 | 390 | 368 | 382 | 324 | 183 | 183 | 213 | 224 | 201 | 183 | 176 | 179 | 166 | 162 | 161 | 137 | 142 | 157 | 170
Iron | N/A | bar: 2019-07-02 to 2020-06-23
Magnesium | N/A | 5.93 | 5.77 | 5.85 | 7.51 | 7.92 | 10.9 | 10.6 | 11.3 | 9.57 | 4.69 | 4.69 | 5.98 | 6 | 5.64 | 5.34 | 4.69 | 4.79 | 4.33 | 4.12 | 3.67 | 3.72 | 4.21 | 4.26 | 6.13
Aluminium | ≤300 | 92.8 | 80.5 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | <50 | 117 | 117 | 89.7 | 84.2 | <50
E.coli | ≤1 | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detected | Not Detetcted | Not Detected | Not Detected | Not Detected